## Handover Checklist (old) (hidden)
SCADA Systems Handover Checklist
| Site Name: |  | #REF!
| Project Number: |  | #REF!
| Project Name: |  | #REF!
RTU Config version number
HMI Config version number
Contacts
| SCADA Manager |  | #REF! |  | Substation Design | #REF!
| SCADA TAT |  | #REF! |  | Protection Design | #REF!
| SCADA Pre-comm |  | #REF! |  | Prot. Commissioning | #REF!
| Completion |  |  |  |  | Outstandings
|  | Uploaded - RTU Config |  |  |  | Item | Description |  |  | Date Completion anticipated | Date Completed
Uploaded - HMI, Ion Meter (where applicable)
File Drawing revisions on USB Stick & LAN
|  | New Hardware serial numbers recorded on Asset Register |  |  |  | 1
|  | Site Photos updated in supvcom directory |  |  |  | 2
|  | Completed Tick and Flick |  |  |  | 3
|  | New firmware appldef files on LAN (where applicable) |  |  |  | 4
|  | Completed “As Constructed” drawings |  |  |  | 5
|  | Email to SCADA Field Staff advising of completion |  |  |  | 6
7
8
9
10
11
12
[6 empty] | Sign Off by TAT or Team Leader |  |  | Date:
THIS SECTION TO BE COMPLETED BY SCADA FIELD STAFF
SCADA Field Group Check
Check Uploaded - D20, PLC and Notes
Check Uploaded - HMI, Ion Meter (where applicable)
Check New Hardware serial numbers recorded in SITIS
Check Site Photos updated in supvcom directory
Review Completed Tick and Flick Issued
Check firmware and hardware records are updated and/or on LAN (SITIS)
|  | Site Visit | Check Site Disk contents
Check Hard copy of Site Drawings
Check Cubicle sealed against ingress of rodents
Check MOXA Wesmaint Connections can be easily unplugged (ie RJ45 to DB9 adapters used at MOXA)
Leave RatSak in Cubicle
|  | Outstandings Accepted at handover |  | Date:
|  | Outstandings Completed after handover |  | Date:
COMMENTS:
ACCEPTED/NOT ACCEPTED
[6 empty] | Sign Off by Field Mtce |  |  | Date:

## Preface
Telecommunications, Automation and Protection Checklists
Templates
Version: | 1
DOCUMENT HIERARCHY
This document resides within the Planning component of Western Power’s Asset Management System (AMS).
DOCUMENT DATE
This document was last updated July 2026
IMPLEMENTATION DATE
This document came into service July 2026
DOCUMENT CONTROL
Record of endorsement, approval, stakeholders, and notification list is provided in ID05-1343104688-601141. This document itself is not controlled but is a compilation of controlled documents, for information only.
RESPONSIBILITIES
Western Power’s Engineering & Design Function is responsible for this document
CONTACT
Western Power welcomes your comments, questions, and feedback on this document, which can be emailed to standards.excellence@westernpower.com.au
DISCLAIMER
This document is published by Western Power for information purposes only. The user must make and rely on their own inquiries as to the quality, currency, accuracy, completeness, and fitness for purpose of any information contained in this document. Western Power does not give any warranty or make any representation concerning the information provided in this document. By using the information in this document, the user acknowledges that they are solely responsible for obtaining independent professional advice prior to commencing any project, activities, or other works. Western Power is not liable in any way for any loss, damage, liability, cost or claim of any kind whatsoever (including responsibility by reason of its negligence) arising from or in connection with the use of or reliance on the information contained in this document. Western Power reserves its rights to modify, supplement or cancel this document or any part thereof at any time and without notice to users.
COPYRIGHT
© Copyright 2026 Electricity Networks Corporation trading as Western Power. All rights reserved. No part of this work may be reproduced or copied in any form or by any means without the written permission of Western Power or unless permitted under the Copyright Act 1968 (Cth). Product or company names are trademarks or registered trademarks of their respective holders
© Western Power
ABN 18540492861

## Whats in this document
Guide to this collation of sample checklists:
References which support implementation of this document. Those listed under title are available separately, the hyprlinks in this sheet relate to an adjacent tab in THIS sheet.
These documents describe processes and standards described in Automation Design Guideline Any reference to Western Power -" Automation Design guidelines" please refer to the documents and checklists listed below
Title
G (P) - Automation Customer Interface Guideline
T (P) - Automation customer interface list
P (P) - Automation project execution | SCADA Automation Quality '!A1
G (P) - Protection Design Guideline
G (P) - Automation Customer Interface Guideline
DS (P) Telecommunications Design Standard | Telecomms Pre-comm Quality'!A1 | Automation project spares'!A1 | Automation Material disposal'!A1
Telecomms Commissioning - Equipment precommissioning checklists | Telecoms XMC
Telecoms CISCO
Telecoms GE ORBIT RADIO
Automation - DNP IED
Automation - Gateway
Automation - GPS Clock
Automation - Layer 2 Network
Automation - Layer 3 Router
Automation - MMS IED
Automation - Redundant Network
Automation - Standalone HMI
Automation IO Module

## SCADA Automation Quality
SCADA Automation and Control Project Quality Checklist | [9 empty] | P 1/1
PROJECT LOCATION: | [6 empty] | PROJECT Name & No:
WORK LOCATION: | [6 empty] | Substation No: (SSxxx)
No: | TASK
1 | Preparation |  |  |  | Workshop | Site | Comments |  | Initial | Check
1.1 | Drawings and materials checked & identified
1.2 | New items accounted (Cubicle, Gateways,Switches, MCBs, links, terminals, labels,etc) - (as per Material lists)
2 | Workshop Build |  | References |  | Workshop | Site
2.1 | Internal Equipment is installed as per design drawings |  | DDA# |  |  |  | Drawing & Revision
2.2 | Point to point wiring checks completed | [5 empty] | Copy of test sheet attached
2.3 | Wire size & type correct as per application and design |  | 6.2.4 | Table 3.1
2.4 | Traversing door/swing frame does not impact internal or externally mounted equipment or cables. | [5 empty] | Photo to be attached
2.5 | Swing frame stay wire/door stop mounted correctly |  | 6.2.13 |  |  |  | Only valid for non-resttrained cubicles, new standard cubicle has fixed restraint
2.6 | Ducting is correct size and lids are fitted.
2.7 | Correct terminals installed as per design. |  | 6.2.6 |  |  |  | Including shielded RJ45 connectors where applicable.
2.8 | Correct MCBs installed as per design. |  | 2.5.2
2.9 | Lugs/Bootlaces are crimped correctly. |  | 6.2.6 |  |  |  | Photo evidence required
2.10 | Terminations are correct as per design and tight. | [5 empty] | Tug test to be applied to confirm.
2.11 | Cable markers and label ferrules applied correctly. |  | 2.5.4 | 6.2.1
2.12 | All earths are connected, earth bars are linked, doors & gland plates earthed, RJ45 connectors shielded |  | 2.5.3 | 6.2.2 |  |  | Shielding and earthing to be considered.
2.13 | All wiring neatly loomed and secured.
2.14 | Fibre loomed and neatly Velcro tied and Fibre support trays installed. |  | 6.2.5
2.15 | Fibre and copper cables clear of swing frame/door. |  | 6.2.3
2.16 | All labels fitted and correct as per design. |  | 2.5.4 |  |  |  | Equipment labels and cable numbers
2.17 | Self Drilling TEK screws not used to secure new Peripheral cards. | [5 empty] | Tek screws must not be used to mount equipment requiring future removal
3 | Field Construction
3.1 | All internal and external cables shall be clearly label at both ends. |  | 6.2.1
3.2 | All cables shall be installed as per Automation Installation PEA instructions and cable route layout. |  | 6.2.3 6.2.5 |  |  |  | Photo evidence required such as installation quality in the duct, on the tray, loom in from rear of the rack to swing frame, top view when swing frame is closed and excess length management.
3.3 | Both the fibre and the receptacle shall be cleaned with appropriate cleaner before it is plugged into the socket. |  | 6.2.5
3.4 | Light continuity end-to-end test for all cores in MTP and ensure both ends are cross. | [5 empty] | Test result required
3.5 | Continuity end-to-end test for all DC supply, data and alarm cables, | [5 empty] | Test result required
3.6 | Copper based media shall be properly installed. |  | 6.2.9
3.7 | All wiring neatly loomed, secured and diversed route when required.
4 | Finishing- Refer to Commissioning Section in EDM# 43264661 for details |  | References |  | Workshop | Site
4.1 | Cabinet/Equipment clean. |  | 6.2.12
4.2 | Automation schematics: red line drawings completed. |  | 2.8.1 |  |  |  | Copy of markup in QVS package
4.3 | Site notes file and applicable work instructions on site disk. |  |  |  | N/A
4.4 | Site disk contains latest revisions of equipment configurations. |  |  |  | N/A
4.5 | Serial numbers, firmware, licences & details recorded in Asset Register | [5 empty] | Starting row number reference in Assets spreadsheet or image attached to sheet.
Overall Comments
4 | Final Inspection/Quality Verification
4.1 | Above Signed Items Complete |  | Sign: |  |  |  | Pay No: | Date:
Name
4.2 | Exceptions:
4.3 | Exceptions Signed Off |  | Sign: |  |  |  | Pay No: | Date:
Name
| Reference: | Internal Western Power documentation is available to accredited vendors
Completed QVS Sheet and applicable artefacts are to be placed into a zip file and stored in the Qualtiy Folder as referenced above.

## SCADA to Maint handover
Template REV 4.15 F.Mularczyk 4/2/2026
SCADA Project to Maintenance Handover Checklist/Project Sign Off
| Site Name: |  | site name
| Project Name: |  | project name
| Project Number: |  | Txxx
| PEA Number: |  | 12345etc
| Volt No/link: |  | DOCUMENT NUMBER
This document can be saved into the Automation Handovers folder
When saving this document use the following naming convention: Commissioning Handover Checklist for *Project No' and *Substation Name*.
This handover shall be supplied to SCADA FIELD TEAM as soon as possible as per below guidelines.
Nb**RED text = requirements/Comments** for guide to what shall be done (Over write in Black this should happen automatically) text for specific
Details/notes/comments to be entered)
Nb** BLUE text = Instructions on what to do in that section
ED = Automation Engineering Design SFM = Scada Field Maintenance EDQ = Engineering Design QA
This Handover/signoff document is made up of 3 sections; 1. Preliminary Works Notification 2. Handover to SCADA Maintenance
3. Final Project Signoff (Asset Performance).
SECTION 1 PRELIMINARY WORKS NOTIFICATION TO SCADA MAINTENANCE(SFM) FROM ENGINEERING DESIGN(ED)
This is the preliminary notification to SFM that works have started on site which may affect issues/equipment relating to SFM.
This would include any equipment/alarms etc that could generate alarms on system or affect exsisting equipmet operation
such as installation of new IED's,I/O cards etc. Start of site works/commissioning.
SECTION 2 HANDOVER TO SCADA MAINTENANCE FROM ENGINEERING DESIGN(ED) (This maybe include multiple stages)
When is a Handover required?:
For New Sites, Substantial additions (61850, upgrades, Relay/card additions, PPG additions, PLC control scheme changes etc):
Handover shall be sent to “Contract Manager” as soon possible after final commissioning done.
N.B Handover shall not be delayed by QA of site.
Config changes.
Completion/Handover Content:
Ensure that all relevant details are passed on through this handover. Issues such as new hardware types, config tools etc should have
already been identified to SCADA FIELD TEAM at time of project scoping/design/implimentation. If not then please pass on that information.
Please provide SCADA FIELD the opportunity to attend site for orientation/training.
Fill in ALL items in check boxes and identify that there are outstandings in tick box in this document and also record all individual items in
Outstanding items register.
For all USA, greenfield and projects which require a new rack build, the SCADA Automation Quality Verification Checklist
SECTION 3 FINAL PROJECT SIGNOFF (Asset Performance)
A handover can be accepted if outstanding items still exist, as long as these items are registered in the SCADA Handover Outstanding Items
checklist, have appropriate actions assigned and accepted, and are tracked to resolution in handover meetings.
SECTION 1 STAGE # PRELIMINARY WORKS NOTIFICATION TO SFM (Duplicate entry per stage if required)
YES
NO
N/A
Notification to SFM to inform of pending works that will/may interfear with current SCADA site. SFM should not be called out to attend site or
problems which maybe caused by project works if they have not been pre informed of those works.
For additional stages copy and insert the whole of section 1 again. Update the heading with the new STAGE# and update details. Number stages
| NEW SITE: |  | Abbrieviation/Drawing series |  | Site Abbreviation / Drawing series SS---
| DATE/S OF WORKS: |  |  | STAGES | From: | To: | Comments:
| Date of works |  |  |  | dd/mm/yyyy | dd/mm/yyyy | Comments if any?
If dates of each stage cannot be identified then a separate Preliminary Handover with relavent stage number will have to be sent for each stage
See EMAIL/DOCUMENTATION section.
EMAIL/DOCUMENT SENT TO:
Emails sent shall have heading starting with "PRELIMINARY HANDOVER ¦ stage number if applicable ¦ sitename ¦ Project No ¦ PEA No"
e.g PRELIMINARY HANDOVER - stage 1of2 - MU9 Transformer upgrade - Project No - PEA No
Emails shall include a copy of this document attached/link. Include necessary relevant information.
***NB - ONLINE "Automation Handover Register" Must be input/updated before sending Preliminary Handover
| SUBMITTED BY: |  | Name: |  | Phone | Date | Organisation/company
| ROLE |  | Name |  | Number | dd/mm/yyyy | WP/Company/Customer etc
If person submitting this notice is not site contact for maintenance queries, then supply those details below.
| ROLE |  | Name |  | Number |  | WP/Company/Customer etc
| ROLE |  | Name |  | Number |  | WP/Company/Customer etc
| OTHER NOTES: |  |  |  | Relevant Details
SECTION 2 STAGE #____ HANDOVER TO SCADA MAINTENANCE (Duplicate entries per stage if required)
Engineering design are responsible for site/items they have Installed/modified/commissioned until handover has been given/accepted by SFM
The sooner this works has been handed to SFM the sooner they will be responsible for it. Add additional Section 2 stages "#", as required.
For additional stages copy and insert the whole of section 2 again. Update the heading with the new STAGE# and update details. Have required
number of blank stages before you start filing in first stage.
|  | DETAILS | Summary of this stage
|  | DATE | dd/mm/yyyy
Any check box items that are blank or have "No" as entry in this section, become an outstanding item that you are required to list and also
put into "Outstanding items register"
|  | Remote access/SOE for site |  |  | DETAILS | Is all required remote access available?/Is all required SOE available on corp
web?
|  | New Equipment TYPE read details |  |  | DETAILS | If first ever use of this equipment by WP ? Supply detail & spare
Nb This is NOT the install of currently used standard new items
|  | Notes file updated |  |  | DETAILS | Exsiting site check and update. Including removal of irrelavent data.
If new site; Use the notes file template to create.
|  | New hardware details updated in |  |  | DETAILS | Full details/ Part number (complete)/ firmware/ serial No/licenses/
|  | Asset register |  |  |  | Equipment name (site) etc
IP register
|  | Location of test sheets |  |  | LOCATION | Location of ED test sheets etc
|  | Work instruction New/Updated |  |  | EDM No | DETAILS PLC-control function-SCADA operations documents etc
Ready for handover
|  | Master Station control functions |  |  | DETAILS | Schemes/items from Master station/other that automatically initiate controls
etc, this Includes setpoints, runback, tripping schemes. NOT normal operator
initiated controls
|  | Site Comms links "Master Station" |  |  | DETAILS | New and comms changes, Master Station Comms page checked for accuracy
and functionality. Including Circ ID, single/dual port, slave DCS devices etc
|  | Drawings & Site labelling updated |  |  | DETAILS | All SCADA drawings (relevant to handover) available on site including any
|  | Also drawing location in WP system |  |  |  | markups (RED); paper copy. All equipment labelled. Cables/cores
labelled and match drawings.
[5 empty] | LOCATION | Drawing location in WP/contractor system (markups etc)location if not issued
|  | Site USB & VoltUpdated |  |  | DETAILS | Updated with all running equipment configurations, notes file, PLC etc
|  | Site Photo's Updated |  |  | DETAILS | Comments?
|  | Drawings all final issue |  |  | DETAILS | All SCADA drawings have final issue? If not, to become outstanding item.
OUTSTANDINGS:
All outstanding items shall be appropriately entered into the "Outstandings register" with item number (items numbers start at
1,2,3 etc per PEA). The fields that must be entered in Outstanding register are:
¦ SITE ¦ EDM(PEA) Reference ¦ DETAIL ¦ Item Number ¦ Raised by ¦ Date Raised ¦ Action Assigned To ¦ Expected Resolution Date ¦
|  | ED Outstandings in Register |  |  | DETAILS | Y=In Register N= not in register N/A=There are no outstandings
|  | EDQ Outstandings in Register |  |  | DETAILS | Y=In Register N= not in register N/A=There are no outstandings
**Inform SFM QA of new outstandings in addition to ED ones
|  | SFM Outstandings in Register |  |  | DETAILS | Y=In Register N= not in register N/A=There are no outstandings
**Paste outstandings into Acceptance/Rejection email
HANDOVER:
|  | Emailed to: |  |  | <Western Power Contract Manager>
Emails sent shall have heading starting with "FINAL HANDOVER ¦ stage number if applicable ¦ sitename ¦ Project No ¦ PEA No"
e.g FINAL HANDOVER - stage 1of2 - MU9 Transformer upgrade - Project No - PEA No
Emails shall include a copy of this document attached/link. Include necessary relevant information.
***NB - ONLINE "Automation Handover Register" Must be input/updated before sending FINAL Handover
ENGINEERING DESIGN (Commissioning group)
Handover to SFM by
|  |  |  | Date: | dd/mm/yyyy |  | By: | Name
Comments:
SCADA FIELD MAINTENANCE
|  | Site Visit |  | Date: | dd/mm/yyyy |  | By: | Name
Comments:
|  | ACCEPTED/PROVISIONAL/REJECTED |  |  | Cross out not applicable outcome
|  |  |  | Date: | dd/mm/yyyy |  | By: | Name
Details:
SECTION 3 FINAL PROJECT SIGN OFF BY ASSET PERFORMANCE
For automation asset handover, E&D & AP will reference this Handover Checklist. Asset Performance when signing off on this completion
should ensure that all work and outstandings are completed, allowing the Project Manager to close out the project.
ASSET PERFORMANCE - SCADA & TELECOMMUNICATIONS
|  | Date: | dd/mm/yyyy |  | By: | Name
Notes:

## Automation project spares
Automation Record
Handover of Project Spares & Recovered Equipment to Maintenance
| DELIVERED BY: |  | DATE:
PROJECT:
THE ITEMS LISTED BELOW WERE PROVIDED:
| Item Description | PO Order | Recovered Site | Quantity | Condition (New/Working/ Not Working)
| RECEIVED BY *: |  | DATE:
DELIVERY LOCATION:
 Note: If no-one is available to receipt on delivery, mark “No-one Available” and specify in the email
This form is to record all SCADA equipment that is recovered from a project and provided to Maintenance as potential Spares. All equipment should have a condition assessment. A hard copy is to be provided with the equipment and a copy (electronic, scan or photo) shall be emailed to: <Western Power Contract Manager>

## Automation Material disposal
Automation Record Equipment Disposal and Write Off
| COMPLETED BY: | [5 empty] | DATE:
THE ITEMS LISTED BELOW ARE TO BE DISPOSED:
| Equipment / Asset # | Item Description |  |  | Serial Number | EGI |  | Reason for Disposal | Cybersecurity Requirements met (Y/N)
Return for Disposal
| Damaged |  | = DA | Uneconomical for Repair | = UR
| Lost |  | = LO | Return to 3rd Party Owner (eg Telstra) | = RO
| Obsolete |  | = OB | Incorrect Entry | = IR
TECHNICAL OPERATIONS ENDORSED BY: | [7 empty] | DATE:
AP S&T ASSET CUSTORDIAN AUTHORISED BY: | [7 empty] | DATE:
This form is to record all Telecommunications equipment that is to be disposed. A hard copy is to be provided with the equipment and a copy (electronic, scan or photo) shall be emailed to the Contract Manager

## Automation - DNP IED
Commissioning Sheet IED DNP
All completed documents to be stored in the Quality folder under a single Substation Collection.
Site _____________________________ Project __________________________
DNP3 Link Testing
Confirm device naming in Gateway aligns with name on equipment on site.
Confirm class and integrity polls to devices are working correctly (use Gateway/RTU Trace). Confirm status and analogs are updating with class poll.
Fail serial comms at Device confirm Device defective alarm is raised at Master Station. Confirm that other relays on the link continue to communicate
If Serial - Confirm Terminals (New Installation) are installed with links on the equipment side of the bus so that equipment can be isolated from link without disrupting the link.
Confirm Surge arrestor or Converter is installed at RTU/Gateway on link to provide isolation.
Confirm Cables to relays and between panels are labelled and screen is earthed
Confirm Terminating resistors is installed on RS485
Confirm Gateway Automatic Polling is setup as per template settings
If IP - For dual ported relays fail ethernet connection 1 at a time and confirm that DNP communications remains/returns within 60s. Also confirm no defective reported from switch for IED failure. Confirm protection network defective alarm is reported for loss of fibre.
If IP - Confirm that remote access has been setup for device. Confirm Connectivity/firmware/Config Compare & Data CAMs function. Passwords saved in the remote access system.
Time Testing
For equipment with IRIG Defective point disconnect IRIG and confirm time sync alarm.
For new equipment with IRIG, DNP3 or NTP Time sync confirm equipment time is synchronised to clock. For existing equipment put the GPS clock into test mode and adjust the time by 5-10 minutes and confirm relays update time, then change back. Confirm all devices have returned to the correct time.
Equipment |  |  | Checked
Name | RTU Port/IP Address | DNP3 Address | DNP3 | TIME
Notes
Completed By ____________________________ Date ______________________

## Automation - Gateway
Commissioning Sheet - Gateway
All completed documents to be stored in the Quality folder under a single Substation Collection.
Site _____________________ Device_____________________________ IP Address __________________________
Physical Inspection | Checked
Equipment and associated MCB is labelled correctly. As per drawing.
All Wires/Cables are labelled
Chassis and Power supply earth is connected
Equipment/Cables are secure are not contacting equipment or being squashed, also check equipment can be removed for replacement and cables/ducting is not in the way
Serial Number/Firmware/Licence is recorded in asset register. Confirm correct Device Name used.
Settings
Firmware is current Western Power Standard Firmware____________________________
Settings have been saved to site disk and Volt
Correct Password is on equipment
No warnings remaining on config
Confirm Gateway is synchronised to IRIG or NTP server
Commissioning General
Review communication statistics for connected devices after 24 hours and confirm maximum 1-2 errors
Fail fibres one at a time and confirm Remote and Local Alarms and that everything remains online
Reboot Gateway and confirm communications is restored to POA and field devices after reboot
Confirm that remote access has been setup for device. Confirm Web and firmware/Config Compare CAMs function. Passwords saved in the remote access sytem.
Confirm Syslog is being updated for device and device name is correct
Confirm SOE is enabled and logging points. No heartbeats are to be mapped.
Redundant Gateways - Confirm Hot Standby ENABLED for all Master and Slave applications
Redundant Gateways - Confirm Virtual IP running. Socket bind on Master and Slave applications address assigned to Virtual IP.
Redundant Gateways - Confirm both main and backup redundancy links running and alarm when failed
Commissioning Master Station LRU
Disconnect Master Station communication links 1 at a time and confirm Gateway fails over to backup and then returns to main when backup is failed, Confirm NO REPLY events have updated at the Master Station as part of failover test. Confirm COM displays show site as dual ported
Fail both links to gateway and confirm other sites on same Master Station channels are not impacted
Reboot gateway and confirm other sites on same Master Station channels are not impacted
Single Ported Sites only - Fail single port to RTU and note that site fail but no attempt is made to search through FEPs if it is a multi drop site. Reboot RTU and check no impact on other sites.
Customer Sites Only (Market Generators) - Confirm 30 second Comm Fail delay is functioning on both fault and planned channel failover. Have OSS perform channel failover and confirm Master station Comms Fail alarm to customer remains NORMAL. Fault channel by removing link 1 and confirm fails over with No alarm. Then Disable comms longer than 30 seconds and confirm it ALARMS. Restore and fail both links locally and confirm it ALARMS after 30 seconds. AEMO requirement to move Gateway onto a new channel without alarming.
Confirm the communications page is correct for the new LRU (RTUs on channel, Circuit ID's, Channel numbers, topology)
Confirm no outstanding commissioning tags or notes on Master station relating to project
Confirm comms displays show interfaces to external sources such as PPG’s, Power produces (WF etc etc), DCS systems and any other data source not part of the standard site equipment.
Notes
Completed By ____________________________ Date ______________________

## Automation - Layer 2 Network
Commissioning Sheet Layer 2 switch
All completed documents to be stored in the Quality folder under a single Substation Collection.
Site _____________________ Device______________________________ IP Address ___________________________
Physical Inspection | Checked
Equipment and associated MCB is labelled correctly. As per Drawings.
All Wires/Cables are labelled
Chassis and Power supply earth is connected
Fibre support bracket in place
Equipment/Cables are secure are not contacting equipment or being squashed, also check equipment can be removed for replacement and cables/ducting is not in the way
Serial Number/Firmware/Licence is recorded in asset register
Config
Reboot switch prior to confirming settings
Firmware is current Western Power Standard Firmware____________________________
Settings have been saved to site disk and Volt
Correct Password is on equipment
No Standing alarms in place
Confirm RSTP Status - Root Bridge - [Root Bridge, Backup Root Bridge, Non Root]. The Switch 1 of the layer 2 switched network must be the Root Bridge. All ports forwarding and designated.
Confirm RSTP Status - Backup Root Bridge [The backup root bridge correctly identifies the Root Bridge is via its direct TRUNK connection, confirm correct MAC address. On a two switch setup loop ports will be shown as alternate/discarding.] Fail the Root bridge by powering down, the backup should now take on the role of Root Bridge.
Confirm RSTP Status - Non Root Bridge (Switch 3 & 4) [The Non root bridge switch correctly identifies the Root Bridge is via its direct TRUNK connection, confirm correct MAC address. On a multiple switch setup loop ports will be shown as alternate/discarding.] Fail the Root bridge by powering down, the backup should now take on the role of Root Bridge and be identified via the TRUNK port.
Confirm Switch is synchronised to Router NTP server. NTP server is the Network Gateway address of the subnet the switch resides.
Commissioning
Confirm that can ping from switch to local networks
Fail fibres to switches, routers, clock one at a time and confirm Remote and Local Alarm
If Switch is part of redundant network complete redundant network testing commissioning Sheet
Switch Off witch confirm remote alarm
Confirm that remote access has been setup for device. Confirm Web/SSH and Connectivity, Firmware, Config Compare CAMs function. Passwords saved in remote access system.
Notes
Completed By ____________________________ Date ______________________

## Automation - MMS IED
Commissioning Sheet IED MMS
All completed documents to be stored in the Quality folder under a single Substation Collection.
Site _____________________________ Project __________________________
Ethernet Testing
Confirm device naming in Gateway aligns with name on equipment on site.
Confirm quality of device defective is included with defective logic from MMS relays by forcing off
For dual ported relays fail ethernet connection 1 at a time and confirm that MMS communications remains and that relays do no report goose defective. Also confirm no defective reported from switch for IED failure. Confirm protection network defective alarm is reported for loss of fibre
GOOSE Testing
Confirm all relays online and not reporting GOOSE defective
Enable Heartbeat and confirm it appears on all relays involved in GOOSE scheme
Disconnect IED fibres to relays sending GOOSE.
Confirm that relays receiving GOOSE from IED report GOOSE defective. GOOSE mapping spreadsheet should be used to confirm.
Repeat for all relays sending GOOSE.
When testing GOOSE defective point these should be forced at the Gateway to confirm correct commoning
Confirm that remote access has been setup for device. Confirm Connectivity/firmware/Config Compare & Data CAMs function. Passwords saved in remote access system.
Goose Send | Receiving Relays |  | LOC ALM | XA ALM
NTP Testing
Confirm relays are listed on NTP servers at router as a client
Stop/Disable NTP main and backup servers.
Check all NTP IEDs report NTP time sync defective.
Commission time sync defective points for individual relays by forcing time sync defective point for particular relay.
Equipment |  |  | Checked
Name | Role | IP | ETH | NTP | GOOSE
Site Inspection |  |  |  |  | Checked
Confirm all Rooms and RIO panels have maintenance port plugged into switch per protection. 1 per location only
Confirm all fibre patch leads are labelled at Relay and Automation Panel
Notes
Completed By ____________________________ Date ______________________

## Automation - Redundant Network
Commissioning Sheet Network - Redundant
All completed documents to be stored in the Quality folder under a single Substation Collection.
Site _____________________________
Record Site Toplology - Only record Router and Switch interconnections.
Normal Operation | Checked
No Standing alarms in place
Confirm Global RSTP Status is correct on all equipment based on role (Root Bridge, Backup Root Bridge, Non Root)
Confirm RSTP Status - Backup Root Bridge [The backup root bridge correctly identifies the Root Bridge is via its direct TRUNK connection, confirm correct MAC address. On a two switch setup loop ports will be shown as alternate/discarding.] Fail the Root bridge by powering down, the backup should now take on the role of Root Bridge.
Confirm RSTP Status - Non Root Bridge (Switch 3 & 4) [The Non root bridge switch correctly identifies the Root Bridge is via its direct TRUNK connection, confirm correct MAC address. On a multiple switch setup loop ports will be shown as alternate/discarding.] Fail the Root bridge by powering down, the backup should now take on the role of Root Bridge and be identified via the TRUNK port.
Confirm VRRP Status is correct on routers for all instances. Only one router should ever be master. Under normal conditions the prime router is MASTER for ALL instances. (Prime Router active, Backup Router backup)
Confirm IP Sec is currently active through prime router
Confirm NTP clocks are listed under NTP and all NTP IEDs are clients at Prime router
Confirm Firewall is enabled and is the current version as per settings guide
Confirm all IEDs are online
Fail Prime Router
Confirm Remote Alarm and Local alarms on connected network equipment
All IEDs should remain online. Expect a brief communication loss as some TCP sessions may need to reestablish, approx. 30 seconds.
Backup router should takeover VRRP and become Root Bridge. Check global RSTP status and VRRP status.
IPSEC connection should re-establish through backup router
Confirm remote connection to devices using backup IPSEC tunnel.
Confirm syslog using backup IPSEC tunnel.
IEDs should connect to backup router for NTP
Restore prime router and confirm normal operation again
Fail Backup Router
Confirm Remote Alarm and Local alarms on connected network equipment
All IEDs should remain online
No impact of VRRP, RSTP, NTP and IPSEC
Fail P1 Root Bridge
Confirm Remote Alarm and Local alarms on connected network equipment
Dual Ported IEDs should remain online single ported IEDs on failed switch only should fail
GOOSE defective should only be reported for loss of single ported IEDS
Backup root bridge should become Root Bridge. Non Root bridge switches should show the change in Root bridge. View via RSTP Port Status.
Fail P1 Backup Root Bridge
Confirm Remote Alarm and Local alarms on connected network equipment
Dual Ported IEDs should remain online single ported IEDs on failed switch only should fail
GOOSE defective should only be reported for loss of single ported IEDS
Root bridge should be unchanged
Fail P2 Root Bridge
Confirm Remote Alarm and Local alarms on connected network equipment
Dual Ported IEDs should remain online single ported IEDs on failed switch only should fail
GOOSE defective should only be reported for loss of single ported IEDS
Backup root bridge should become Root Bridge
Fail P2 Backup Root Bridge
Confirm Remote Alarm and Local alarms on connected network equipment
Dual Ported IEDs should remain online single ported IEDs on failed switch only should fail
GOOSE defective should only be reported for loss of single ported IEDS
Root bridge should be unchanged
Link Failure Testing
Fail main SEAL connection on Prime Router. SEAL IPSEC connection should establish to backup router.
Fail links between router and switches 1 at a time, confirm all IEDs stay online and local and remote alarms
Fail links between switches confirm all IEDs stay online (in case of trunk 2x1000FX links fail both links) and local and remote alarms
Fail links to NTP clock and confirm local and remote alarms
Notes
Completed By ____________________________ Date ______________________

## Automation - Standalone HMI
Commissioning Sheet Standalone HMI
All completed documents to be stored in the Quality folder under a single Substation Collection.
Site _____________________ Device_____________________________ IP Address __________________________
Physical Inspection | Checked
Equipment and associated MCB is labelled correctly
All Wires/Cables are labelled
Chassis and Power supply earth is connected
Equipment/Cables are secure are not contacting equipment or being squashed, also check equipment can be removed for replacement and cables/ducting is not in the way
Serial Number/Firmware/Licence is recorded in asset register
Settings
Firmware is current Western Power Standard Firmware____________________________
BIOS is current Western Power Standard BIOS____________________________
Settings have been saved to site disk and Volt
Correct Password is on equipment
Commissioning General
Remote access functional. Passwords saved in remote access system.
Reboot HMI, powers up into Operator mode and RUNNING. No pop up boxes or errors.
HMI hardwired/software alarm is functioning.
STOP HMI database. Confirm VDU Mimic alarms at Master Station & SOE.
Confirm Windows firewall ENABLED
Commissioning Network
Confirm HMI ethernet ports in BRIDGE mode, static IP applied and DHCP DISABLED.
Confirm router is synchronised to the Automation NTP server.
Disconnect the Patch to Port 1, confirm successful communications via Port 2.
Disconnect the Patch to Port 2, confirm successful communications via Port 1.
Notes
Completed By ____________________________ Date ______________________

## Automation IO Module
Commissioning Sheet I/O Module
All completed documents to be stored in the Quality folder under a single Substation Collection.
Site _____________________________ Project __________________________
Physical Inspection | [5 empty] | Checked
Power wetting and ethernet cables are labelled
I/O Module earthed as per drawing
Serial Number/Firmware/Licence is recorded in asset register
I/O Label cut and sitting on terminals correctly
Config | [5 empty] | Checked
Firmware is current Western Power Standard Firmware____________________________
Settings have been saved to site disk and Volt
Correct Password is on equipment
Commissioning | [5 empty] | Checked
Confirm device naming in Gateway aligns with name on equipment on site.
For dual ported Modules fail ethernet connection 1 at a time and confirm that communications remains to Gateway and that a Peripheral Card defective alarm is reported for loss of the link
Fail entire device by pulling power supply, for site with ring topology other equipment should remain online. Confirm peripheral card fail for loss of device.
Confirm I/O Modules are listed on NTP servers at router as a client
Confirm I/O Modules internal clock is synchronised and showing the correct time
For IO modules confirm wetting supply loopback is installed, disconnect and confirm Supply Fail alarm is raised.
Confirm that remote access has been setup for device. Confirm Web/application function. Passwords saved in remote access system.
Equipment |  |  | Checked
Name | Serial No | IP | INSP | CFG | COMM
Site Inspection |  |  |  |  | Checked
Confirm all Rooms and RIO panels have maintenance port plugged into switch per protection. 1 per location only
Confirm all fibre patch leads are labelled at Relay and Automation Panel
Notes
Completed By ____________________________ Date ______________________

## Telecomms Pre-comm Quality
Telecommunications Site Quality Audit
|  |  |  | a |  | x
SITE NAME : | [6 empty] | Audit Type (select from list below)
AUDITOR : | [7 empty] | Photos Available (Please include folder that the Audit photos have been saved to in Comms images)
DATE :
Summary (Overflow to Summary Tab) | Project to Rectify | Main. To Rectify | No Action | Ops TL approved | Non Conformance Risk to Network | Main TL Approved | Completed By & Date | Comments
Non Conformance (please include reference to photo file ID of non-conformance) | To be reviewed and agreed via PM, Telecom Ops and Telecom Maintenance TL |  |  |  | Enterprise Risk Assessment Criteria |  |  | If non conformance applies to a Technical Specification or Comms Standard please reference accordingly (links to standards in references tab)
CR1
[5 empty] | Low |  |  |  | on site
desktop
CR2
CR3
CR4
CR5
Observations
Notes / Questions
SITE ACCESS & GENERAL | OK | NOT OK | N/A | Project | Comments
Site Access Drawing, Contact details ,Safety info and ESA info correct
Communication Logbook on site
Photographs taken of installation
Pax Phone , VOIP Phone Operational (Test call with NMC)
Radio Licenses displayed on site and with correct frequency
RACK 1 | OK | NOT OK | N/A | Project | Comments
Rack Installed and Mounted Securely at Correct Location
Rack In Sound Condition - No Dents/Damages/Scratches/Un-obstructed
Rack Door Labelled - Front & Back
Rack Grounded to Main Earth according to standard
Rack Doors Earthed
Equipment Rack Earth Block Fitted on Insulated Mounts - Top & Bottom
Cable Ladder Installed and earthed
Fibre Trunking/Rugged Fibre/Duct Installed according to standard
RDP Installed according to drawing
RDP A & B Power Cable Installed
RDP Fail - Alarm Cable installed and tested to krone
RDP cable Numbers Labelled
RDP Ground Cable Installed and according to standard (if applicable)
Correct Size Circuit Breakers installed according to drawings
Positive Earth Installed and terminated according to standard (48v Rack at Rack +ve bar / 110v Rack at Rectifier +ve bar)
Protective Earth installed and grounded according to standard (Rack Earth Block)
IDF Frame Installed according to design
IDF ID labelled on right of rack chassis
All tie cables screened and grounded at one end
All cables and krones labelled
Cable glands used for all cables entering racks
Correct cable gland plate entry points used
Unused cable gland plate entry points sealed
All Equipment/Shelves/Frames installed in correct RU position according to drawings
RACK 2 | OK | NOT OK | N/A | Project | Comments
Rack Installed and Mounted Securely at Correct Location
Rack In Sound Condition - No Dents/Damages/Scratches/Un-obstructed
Rack Door Labelled - Front & Back
Rack Grounded to Main Earth according to standard
Rack Doors Earthed
Equipment Rack Earth Block Fitted on Insulated Mounts - Top & Bottom
Cable Ladder Installed and earthed
Fibre Trunking/Rugged Fibre/Duct Installed according to standard
RDP Installed according to drawing
RDP A & B Power Cable Installed
RDP Fail - Alarm Cable installed and tested to krone
RDP cable Numbers Labelled
RDP Ground Cable Installed and according to standard (if applicable)
Correct Size Circuit Breakers installed according to drawings
Positive Earth Installed and terminated according to standard (48v Rack at Rack +ve bar / 110v Rack at Rectifier +ve bar)
Protective Earth installed and grounded according to standard (Rack Earth Block)
IDF Frame Installed according to design
IDF ID labelled on right of rack chassis
All tie cables screened and grounded at one end
All cables and krones labelled
Cable glands used for all cables entering racks
Correct cable gland plate entry points used
Unused cable gland plate entry points sealed
All Equipment/Shelves/Frames installed in correct RU position according to drawings
RACK 3 | OK | NOT OK | N/A | Project | Comments
Rack Installed and Mounted Securely at Correct Location
Rack In Sound Condition - No Dents/Damages/Scratches/Un-obstructed
Rack Door Labelled - Front & Back
Rack Grounded to Main Earth according to standard
Rack Doors Earthed
Equipment Rack Earth Block Fitted on Insulated Mounts - Top & Bottom
Cable Ladder Installed and earthed
Fibre Trunking/Rugged Fibre/Duct Installed according to standard
RDP Installed according to drawing
RDP A & B Power Cable Installed
RDP Fail - Alarm Cable installed and tested to krone
RDP cable Numbers Labelled
RDP Ground Cable Installed and according to standard (if applicable)
Correct Size Circuit Breakers installed according to drawings
Positive Earth Installed and terminated according to standard (48v Rack at Rack +ve bar / 110v Rack at Rectifier +ve bar)
Protective Earth installed and grounded according to standard (Rack Earth Block)
IDF Frame Installed according to design
IDF ID labelled on right of rack chassis
All tie cables screened and grounded at one end
All cables and krones labelled
Cable glands used for all cables entering racks
Correct cable gland plate entry points used
Unused cable gland plate entry points sealed
All Equipment/Shelves/Frames installed in correct RU position according to drawings
RACK 4 | OK | NOT OK | N/A | Project | Comments
Rack Installed and Mounted Securely at Correct Location
Rack In Sound Condition - No Dents/Damages/Scratches/Un-obstructed
Rack Door Labelled - Front & Back
Rack Grounded to Main Earth according to standard
Rack Doors Earthed
Equipment Rack Earth Block Fitted on Insulated Mounts - Top & Bottom
Cable Ladder Installed and earthed
Fibre Trunking/Rugged Fibre/Duct Installed according to standard
RDP Installed according to drawing
RDP A & B Power Cable Installed
RDP Fail - Alarm Cable installed and tested to krone
RDP cable Numbers Labelled
RDP Ground Cable Installed and according to standard (if applicable)
Correct Size Circuit Breakers installed according to drawings
Positive Earth Installed and terminated according to standard (48v Rack at Rack +ve bar / 110v Rack at Rectifier +ve bar)
Protective Earth installed and grounded according to standard (Rack Earth Block)
IDF Frame Installed according to design
IDF ID labelled on right of rack chassis
All tie cables screened and grounded at one end
All cables and krones labelled
Cable glands used for all cables entering racks
Correct cable gland plate entry points used
Unused cable gland plate entry points sealed
All Equipment/Shelves/Frames installed in correct RU position according to drawings
RACK 5 | OK | NOT OK | N/A | Project | Comments
Rack Installed and Mounted Securely at Correct Location
Rack In Sound Condition - No Dents/Damages/Scratches/Un-obstructed
Rack Door Labelled - Front & Back
Rack Grounded to Main Earth according to standard
Rack Doors Earthed
Equipment Rack Earth Block Fitted on Insulated Mounts - Top & Bottom
Cable Ladder Installed and earthed
Fibre Trunking/Rugged Fibre/Duct Installed according to standard
RDP Installed according to drawing
RDP A & B Power Cable Installed
RDP Fail - Alarm Cable installed and tested to krone
RDP cable Numbers Labelled
RDP Ground Cable Installed and according to standard (if applicable)
Correct Size Circuit Breakers installed according to drawings
Positive Earth Installed and terminated according to standard (48v Rack at Rack +ve bar / 110v Rack at Rectifier +ve bar)
Protective Earth installed and grounded according to standard (Rack Earth Block)
IDF Frame Installed according to design
IDF ID labelled on right of rack chassis
All tie cables screened and grounded at one end
All cables and krones labelled
Cable glands used for all cables entering racks
Correct cable gland plate entry points used
Unused cable gland plate entry points sealed
All Equipment/Shelves/Frames installed in correct RU position according to drawings
VOIP Media convertor Cabinet. (Drawings C58/13/1-6) | OK | NOT OK | N/A | Project | Comments
Cabinet Installed and Mounted Securely at Correct Location and height
Cabinet Door Labelled - Including laser warning Label
All cabling within cabinet labelled
Cabinet Grounded to Main Earth according to standard
Cabinet Door Earthed according to standard
Media convertor Earthed according to standard.
Correct Size Circuit Breakers installed according to drawings
Cisco VOIP Handset Installed and Mounted Securely at Correct Location and height
Eaton Rectifier | OK | NOT OK | N/A | Project | Comments
Rectifier Commissioned
Rectifier Management Cable Installed to Patch Panel
Alarm Cable Installed And Terminated At Comms Rack Krone
12V Rectifier (Rectifier Fail) Alarm Cable terminated at Rect.-48V Alarm Board
Battery Midpoint Monitoring Cable Installed On Battery Banks. C481/57/2
Check battery bank lugs are correct size for cable being used
Rectifier In Correct Location For Ac Feeds(Separate Phase Per Rectifier
Main Ac Switchboard, Individual (Not Ganged) (Ac Circuit Breakers, Labelled).
Ac Feeds Protected By Surge Diverters
PLC circuit Breaker is rated to 6amp
Battery Dc Circuit Breakers, Labelled. Battery Banks Labelled
Load Dc Circuit Breakers, Labelled.
Fail Ac Circuit Breaker And Check Alarm Extended To Nmc.
Is Low volt alarm threshhold set to -48v? Check with NMC
Dc Power Systems Earthed According To Standard
Confirm Load Current With Sim Data And Battery Standby Min Met
XMC 23,25 | OK | NOT OK | N/A | Project | Comments
XMC Shelf location in rack installed according to design
XMC Shelf, Fan, Air Deflector and Cable Tray Installed
Fibre management Installed (inverted)
XMC Ground Cable Installed and according to standard (16mm)
XMC Power Cable - A & B Installed and according to standard and drawing (2.5mm)
Cards Inserted according to design and screwed in
Management cable installed to Patch Panel (if applicable)
Circuit Breakers Installed and value according to design
All Cables and fibers labelled
XMC ID number is labelled on right of rack chassis
All Krones labelled
NEC -VR4. | OK | NOT OK | N/A | Project | Comments
IDU
IDU Installed according to design
Shelf Power Cable Installed and according to standard
Circuit Breakers Installed and value according to design
Shelf Ground Cable Installed and according to standard
Alarm Cable Installed
Management cable installed to Patch Panel
RG214 Tail Installed and labelled
Fibre Management Installed
Fibre cable installed and labelled
16xE1 Cabled and tested to krone
All cables labelled
NEC ID number is labelled on right of rack chassis - including licence No, Frequencies and site A and B
ODU
Antenna Installation Complete
Link Alignment Complete
Feeder Installation Complete
Feeder Labelled Indoor/Outdoor
Lightning Arrestors Installed and Grounded
CISCO | OK | NOT OK | N/A | Project | Comments
Cisco Shelf Installed according to design
Shelf Ground Cable Installed and according to standard
Shelf Power Cable - A & B Installed and according to standard
Circuit Breakers Installed and value according to design
Patch Panel Installed and according to design
Patch Panel Grounded
Patch Panel ID number is labelled on right of rack chassis
Patch Panel ports labelled according to drawings
Fibre Management Installed
Ethernet RJ45 Patch cables Installed and tested
RJ45 Cables External to Rack Grounded at Patch Panel
CISCO ID number labelled on rack frame
Teleprotection | OK | NOT OK | N/A | Project | Comments
TPS Shelf installed according to design
Shelf Ground Cable Installed and according to standard
Shelf Power Cable Installed and according to standard
Protection Cabling ready for termination at sak terminal
TPS Alarm cable to SCADA krone prepared
TPS Alarm cables to RTU/XMC terminated at TPS krone
TPS CIRCID labelled on the front and back
Terminal Blocks fitted with protective cover
110v feeds run in barrier conduit
Teleprotection - TEPI | OK | NOT OK | N/A | Project | Comments
**** Under Construction***
The TEPI card shall be located in Slot 14 (XMC23) or Slot 21 (XMC25) in the 48V rack
The terminal block shall reside in the 110V TPS rack. In the absence of this rack or sites with space constraints, a wall mounted cubicle shall be installed to house the terminal block which should be constructed as per the supplied drawings.
Terminal Blocks fitted with protective cover
The TEPI card shall be earthed via an earth terminal installed in the 110V TPS rack din rail terminal strip. The terminal block of the V9UKa cable shall be clipped onto a grounded DIN rail in the MDF. The mounting rail of the V9UKa terminal block shall be connected to rack earth block through a copper wire of ≥ 2.5 mm2
The TEPI V9UKa cable shall be secured to the card via the connectors and shall be checked to ensure it is fastened tightly. Any defect in the clip mechanism shall require a new cable to be installed in its place
The VU9K cable will be installed in black split corrugated conduit (RS part number 755-9017 or equivalent) from the rack entry gland plate to the TEPI card on the multiplexer in order to distinguish it for other multiplexer cables
Black split corrugated conduit labelling as per Telecoms Intallation document
The TEPI VU9Ka cable connector shall have two labels affixed to the connector as shown below. The text shall contain “CAUTION <TPS voltage>V”.
AMI - Access Point. Ref. C54/33/1 through C54/33/5 | OK | NOT OK | N/A | Project | Comments
**** Under Construction***
The wall bracket and associated cables are not to be installed within 2m of Pilot cable isolation cubicles and/or telephone isolation cubicles.
The bottom of the bracket is to be a minimum of 450, preferred 1200mm above the floor level. Frontal clearance is to be a minimum of 900mm.
Earth the wall bracket to the substation earth via 16mm2 Green/Yellow flexible copper cable. Termination at the wall bracket is M6 lug. The AP 6mm2 ground cable to the same point on the wall plate with an M6 lug.
Earth termination at the building ground will be either M10/M12 lug, or 70/120mm2 BASC cable. All lug/cable connections to be hex crimped and fitted with green/yellow heat shrink. All BASC cable connections to be C crimped.
AP earthed via 6mm2 Green/Yellow flexible copper cable fitted with an M6 copper lug to the AP ground point (1/4”diameter-20 TPI x 1/2 long” machine screw). The lug/cable connection is to be hex crimped and fitted with green/yellow heat shrink.
Label the Patch panel port with the AP number on the top line and cable number on the bottom line i.e AP5.01, C030
Label the Cat6A cable - AP5.01 and the provided cable number
Internal RF Tail - Label both ends of the cable 50mm from the end with the AP number i.e AP5.01 with a Brady wrap around label PTL-21-427 or equivalent.
Access Point - Label the Access point with the generation revision and site installation number i.e. AP5.01. This is equipment type: Access Point, Generation: 5, number installed on site: 1
Access Point - Label the Access Point with the Pick Id e.g Belmont Substation is N9121909
Battery Backup Pack -Label the BBP with the site installation number on the top line and installation date on the bottom line i.e BB.01 13.05.2018 with Brady White continuous lable PTL-42-439 or equivalent.
240VAC 10A GPO - AMI – DO NOT TURN OFF with Brady White continuous lable PTL-8-439 or equivalent.
Temporature Sensor Gateway. C52/34/1 | OK | NOT OK | N/A | Project | Comments
Temperature Sensor installed according to drawing
Shelf Power Cable - Installed and labelled according to drawing
Circuit Breaker Installed and value according to design
Ground Cable Installed and according to standard
Management Cable installed and labelled to Patch Panel
TEMP SENS is labelled on right of rack chassis
Fibre Management & FOBOT | OK | NOT OK | N/A | Project | Comments
Cables/Fibres Clearly Labelled.
All Cables Neatly Formed And Secured.(Min 30Mm Bending Radius)
All Fibres Neatly Formed And Secured In Splicing Trays.
No Excess Fibre Stored In Ducts, Ducts Clear Of Construction Debris.
Correct Glands used To Prevent Vermin Entry.
Mast / Tower / Building | OK | NOT OK | N/A | Project | Comments
Safety Climb Fitted.
Anti Climb Fitted
Structure Earthed
Gantry Earthed.
Feeders Earthed (No Tight Radius Bends) And Fitted With Lightning Arrestors.
Feeders Labelled
Building& Fence Installed Correctly And In Sound Condition. Fence And Building Earthed.
Ac Power Feed, Meter And Surge Arrestors Installed Correctly
General Water Runoff Acceptable.
Site Firebreak & Meets Bushfire Protection Standard
Personnel Fire Safety Plan
Network Management & Configuration | OK | NOT OK | N/A | Project | Comments
NMC Acceptance Notice (Template DM# 10031878)
NMC Support Acceptance Notice (Template DM# 10031878)
Fibre Network Acceptance Notice (Template DM# 10031878)
OSS Administration Acceptance Notice (Template DM# 10031878)
Outstanding Items Register (Template DM# 10031878)
NEW HUT - External Alarms | OK | NOT OK | N/A | Project | Comments
Check if alarms have been terminated & tested at krone :
Fire
Surge
Door/Entrance
Air Cond
High Temperature
ADDITIONAL COMMENTS :

## Telecoms XMC precomm
Telecommunications XMC precommissioning checklist
Site:
Network Element:
IP Address:
Chassis |  | XMC25 |  |  | XMC23
Power Supply |  | DUA25 |  |  | DUA23
Fan Unit |  | COOL4 |  |  | COOL6
Management Configured |  |  | Yes | No
Synchronisation Configured |  |  | Yes | No
Shelf Programmed as Per Clarity? |  |  | Yes | No
Test Link Established? |  |  | Yes | No
Details
Number of Cards Installed |  | Slot Numbers | FW Installed |  | SFPs Installed (List all types installed)
COGE5/CENT2
SELI8
STM14 or NUSA1
TUDA1 (V.28/V.11)
TUGE1
TUEM1
SHFI-M or OPIC1/2
SUPM1
TUXA1
ETAG1
VOIP1
ETO12
ETE24
SUP12
TEPI2
Completed By: |  |  |  | Date:
Accepted By: |  |  |  | Date:
Copy when completed, attached to Equipment Box and Commissioning File

## Telecoms CISCO precomm
Telecommunications CISCO precommissioning checklist
Site:
Network Element:
IP Address:
Chassis |  | ASR-920 |  |  | CGS-2520
|  | CGR-1120 |  |  | ME-3400
|  | IE2000 |  |  | ME-3600
|  | IR1101 |  |  | IE4010
Correct Power Supply Fitted |  |  | Yes | No
Correct Firmware Installed (see CSP) |  |  | Yes | No
Configured as per Clarity/CSP |  |  | Yes | No
Shut Trunk Ports down as per Network layout |  |  | Yes | No
Notes. (eg SFP'S missing etc)
SFP's Fitted if required (list SFP type) |  | List Ports SFP's Fitted into |  |  | Notes
Completed By: |  |  |  | Date:
Accepted By: |  |  |  | Date:
Copy when completed, attached to Equipment Box and Commissioning File

## Telecoms GE Orbit Radio Precomm
Telecommunications GE Orbit precommissioning checklist
Site:
Network Element:
IP Address:
Chassis |  | Link (450MHz) |  |  | Base (150 MHz)
PSU (6844) |  |  | Yes | No
Controller (6834) |  |  | Yes | No
Alarm (6848) |  |  | Yes | No
RF Module (6846) |  |  | Yes | No | HP:
Duplexer Installed |  |  | Yes | No | LP:
Labels |  |  | Yes | No
Correct Firmware Installed (see CSP) |  |  | Yes | No
Configured as per Clarity/CSP |  |  | Yes | No
Test Link Established? |  |  | Yes | No
Notes.
Completed By: |  |  |  | Date:
Accepted By: |  |  |  | Date:
Copy when completed, attached to Equipment Box and Commissioning File

## Telecoms Maint handover
Handover Certificate - Telecommunications Design
Project Name
Project Number |  | Handover Certificate no.
Project Manager
Comms Design Engineer
Description of project being handed over
Acceptance checks |  |  | Document Reference (as necessary) |  |  |  | Completed Date |  |  | Outstanding Items Y/N
Project design completed as per Guideline
Provisioning completed
Drawings issued (Please provide DDA EDM)
New sites added to relevant databases (OSS, SIM, SPIDA, Ellipse)
Construction SOW
Commissioning Request
Spares provided in accordance with Strategy (Please provide Spares Handover list)
Asset data provided as per 1427700 )
Safety in Design completed and HMR updated
Introduction of New Equipment (Please provide copy of assessment and new CSP)
Tower / Mast Structural Assessment Certificate and Structural Drawings
Site photos added to LAN
Commissioning Request been signed and returned
Construction Quality accepted
Site work completed as per Commissioning Guideline |  |  | N/A
Site photos added to LAN |  |  | N/A
Drawing Mark-ups submitted to drafting
Commissioning documentation completed
RTU alarms commissioned (Please provide EDM reference/s)
Obsolete equipment recovered/ tagged
Battery records updated
Provisioning updates provided (As necessary)
Outstanding alarms captured?
Physical site audit completed (as required)
| Name |  |  | Signature |  |  |  |  | Date
Commissioner
PM Endorsement
Sponsor Acceptance
Handover Certificate - Outstanding Items Register
All items that are outstanding at the time of handover shall be registered below with clear actions assigned.
Description of outstanding items/ action planned
Identified Issue/ Opportunities for Improvement | Planned Action |  |  |  | Responsible Person |  |  | Additional Document Number |  |  | Action Due Date
#
#
#
#
#
#
#
#
#
#
#
#
#
#
#
| Name |  |  | Signature |  |  |  |  | Date
PM Endorsement
Sponsor Acceptance
Handover Certificate - Acceptance
Technical Operations – Operations Team Leader
Accepted By
Signature | [5 empty] | Date
Technical Operations – Maintenance Team Leader
Accepted By
Signature | [5 empty] | Date
Asset Performance – Automation and Control Area Manager
Accepted By
Signature | [5 empty] | Date

## Comm design and Imp checklist
Communications Design and Implementation - preconstruction checklist
SITE NAME _________________________________
RACK No. _________________________________
WORKSHOP
Equipment delivered in sound condition - no dents -
Damage - scratches
Racks delivered with correct mounting hardware
Rack mounting set backs as per Western Power spec
Cable tray fitted
Racks delivered with gland plates fitted to top and bottom
With all holes sealed
Door keys available and affixed to rack prior to despatch
Dc distribution panel fitted with correct bus and voltage range
Circuit breakers and led's as per site drawings
Equipment rack earth block fitted on insulated mounts
Rack doors earthed (where applicable)
All equipment fitted as per site design drawings
(Any changes to be marked up on design drawings)
All fitted equipment shelves earthed to protective earth block
Idf's fitted and labelled according to site drawings
(Any changes to be marked up on design drawings)
Ddf's fitted and labelled according to site drawings
(Any changes to be marked up on design drawings)
Cable management fitted as per design drawings
All cables fitted are screened and earthed at one end only
Signalling krone earth block fitted as per drawings
Protective krone earth blocks fitted as per drawings
Temperature sensor fitted as per design document
Teleprotection terminal blocks fitted with protective cover
110v feeds run in barrier conduit
Dewar teleprotection units have 50mm hole in rear panel for
Programming access
Rack designation labels affixed front and rear -top of label
250mm from top of door.(site name rack designation)
Rack wrapped for transport in original protective
Cardboard and plinth
Onsite
All tie cables earthed according to standard
All tie cables terminated and tested for continuity
All tie cables conform to termination schedules
DC RDP system checked for polarity and continuity
Equipment layout conforms to design
MUX cards pre-comissioned as per test sheets
Teleprotection units pre-commissioned as per test sheets
Microwave radio units pre-commissioned as per test sheets
Sdh equipment pre-commissioned as per test sheets
DC/DC converters tested and commissioning completed
DC power systems earthed according to design
DC positive feeds for racks are run to rectifier positive and
Not earthed at any other point
Equipment racks earthed according to design
All racks fixed to the floor in a sound manner
And bolted together
Cable ladder fitted as required and earthed
Fibre duct fitted as per design
All on site commissioning completed as required in commissioning
Documents.
End to end commissioning completed as required
Prior to cut overs
Outstanding items to be reported to wpc project manager
CONSTRUCTED BY :- _______________________________________________________
TESTING OFFICER :- _______________________________________________________
DATE :- ________________________________________________________
WPC PROJECT MANAGER:- _________________________________________________
DATE :- _______________________________________________________