## Indoor Substation Checklist
Indoor Substation Checklist v1.0
Distribution Conformance Assessment - Fire Rated Substation Installations
Part A - Design
Purpose: To ensure the requirements for a fire rated/indoor substation installation have been met. The relevant sections of the WA Service & Installation Rules, Distribution Substation Plant Manual, Building Code of Australia and Australian Standards should be consulted for further information and clarity.
Instructions:
1. For each design requirement for PART A ONLY, select Yes, No, or N/A from the dropdown in column D
2. If you select No or N/A, provide a brief explanation in Column E
3. Complete all yellow sections until the status bar at the top indicates "Complete". Incomplete submissions may result in your application being rejected.
Last Updated | 2025-07-11
Part A Status (Office use only) | Incomplete Sections Remaining
Site Address
Date
Name and Company
A.1 General Conditions
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 6.7.1 6.8 6.11 6.13 | Have the following matters been considered and addressed as part of the design preparation: | N/A | N/A
| Correct site identification (including final levels) | N/A
| Land allocation and easement/encumbrance requirements | N/A
| Removal and reinstatement requirements for road reserves, public open space, etc. | N/A
| Environmental and heritage requirements | N/A
WASIR 14.4.3 14.4.4 14.4.6 6.3.2 | A risk and hazard assessment has been undertaken including but not limited to the following: | N/A | N/A
| Location of other existing or proposed structures both on and adjacent to the site | N/A
| Identification of fire zones and fire escape routes | N/A
| Hazardous environments | N/A
| Climatic environmental conditions and flood levels | N/A
| Safety in design | N/A
| Other matters (please state) | N/A
WASIR 14.4.2 | Substation contains no building or other services apart from those shown on the drawings provided by the Network Operator. | N/A
WASIR 14.4.2 | Does the enclosure comply with Government Agencies, Building Code of Australia and Local Government Authority requirements? | N/A |  | Incomplete
A.2 Site Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.6 | The selected site has been designed in accordance with the regulatory and network operators’ requirements including but not limited to acceptable: | N/A | N/A
| Location above adjacent lots/roads, flood levels | N/A
| Location regarding water inundation and vegetation | N/A
| Traffic movement and the need to provide infrastructure/equipment protection eg bollards | N/A |  | Incomplete
A.3 Access and Installation Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.7.1 14.4.7.2 14.4.7.3 | Confirm that site access is suitable for heavy vehicles and plant, and that all access requirements have been considered, including: access route (slope/gradient), cable hauling/pulling eyes, gatic covers (if applicable) | N/A
AS2067 5.5.4 | Minimum access requirements maintained in service areas as per AS2067 5.5.4 where a non-standard design is proposed | N/A
WASIR 14.2.1 | District Substations: Preferably situated on the front street boundary or by agreement with the Network Operator up to a maximum (LV Cable length) of 30m. | N/A |  | Incomplete
A.4 Emergency and Exit Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.5 14.6.4 | Requirements of fire alarm and fixed fire suppression systems are met. | N/A
WASIR 14.4.4.2 AS2419.1-2005 | Fire hydrants and brigade booster assemblies are located in accordance with the standards (located 10m from any HV distribution equipment). | N/A
WASIR 14.4.4.3 | Petroleum and gas installations are located away from any Network Operator electrical equipment or as per WASIR distances. | N/A
WASIR 14.6.6 | Doors (2) are: | N/A | N/A
| Located on alternative walls | N/A
| Self-closing/locking doors, fitted with panic release bars | N/A
| 2hr fire rated (including all associated hardware) | N/A
| Fitted with Network Operator labels as per AS/NZS 1905 | N/A |  | Incomplete
A.5 Civil and Structural Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
DPSM Section 3 | Minimum dimensions and arrangement as per relevant DSPM Section 3 arrangement. | N/A | N/A
| Please detail relevant DSPM drawing | N/A
WASIR 14.3.4.1 DSPM 3 DSM 6 | HV/LV Switchgear and metering unit (if required) support structures have been designed correctly. | N/A
WASIR 14.6.2 | The enclosure to be designed by a chartered structural engineer to accommodate loads and forces as outlined in AS/NZS 1170. | N/A
WASIR 14.6.2 | Substation design has no more than two transformers in the same enclosure, with transformer pairs fire segregated. | N/A
WASIR 14.6.5 DSPM 3 DSPM 5 | Substations housing a transformer have: | N/A | N/A
| brick bund at least 75 mm high at every door location OR | N/A
| alternative bunding | N/A
WASIR 14.6.7 DSPM 3 | Have a minimum ceiling height of 2.5 metres (3 metres where ducting passes over the top of the transformer), roof to be dust tight and all storm water guttering to be external to the room. | N/A
WASIR 14.6.11 | Fire rated certification available/provided. | N/A |  | Incomplete
A.6 Trenches, Ducts and Other Penetrations
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.2 | Allowance for trench surfaces and enclosure floors to be painted with an appropriate sealant. | N/A
WASIR 14.6.8 DSPM 3 | Appropriate trench covers: | N/A | N/A
| Designed correctly (mesh/slab) | N/A
| Supported correctly | N/A
WASIR 14.6.8 | Ducts or other penetrations entering the trench or enclosure are designed with removable watertight seals to both ends of the installed ducts or penetrations (includes earth rod penetrations). | N/A
WASIR 14.6.8 | Where ducts are installed between fire segregated switch-rooms, ducts are designed with 2hr fire rated sealing. | N/A
WASIR 6.10 DSPM 3 DSM 6 | Substation site has the correct cable duct arrangement: | N/A | N/A
| Power (including transformer tails) | N/A
| Earthing | N/A
| Communication | N/A
| Metering | N/A |  | Incomplete
A.7 Ventilation
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.7 AS2067 AS 1682 AS/NZS 1668 DSPM 3 DSM 6-02 | Ventilation designed as follows: | N/A | N/A
| Cooling | N/A | N/A
| Cross flow over transformers | N/A
| Fans located inside room (if forced) | N/A
| Dedicated inlet/outlet outside the building (basement OR non-boundary located) | N/A
| Individual (non-cumulative) ducting per transformer | N/A
| Vent/louvre number/size/type/positions | N/A
| Increased room height (3m) if ducting above transformer/RMU | N/A
| Thermostat installed directly above each transformer and set at 50° per transformer | N/A
| Correct flow rate per transformer | N/A
| Fire/Smoke | N/A | N/A
| Self-closing pressure relief vents | N/A
| Ventilation system is 2hr fire rated | N/A
| Electrical | N/A | N/A
| Supplied from Substation Local DB | N/A
| Correct fan starter wiring | N/A |  | Incomplete
A.8 Light and Power
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.9 AS2067 Cl. 5.1.6 AS/NZS 1680 AS/NZS 3000 | All general and emergency lighting fixtures, GPO’s including all associated wiring has been designed correctly. | N/A
| Substation Local DB (3ph) supplied from Customer SMSB (min. 6sq.mm) | N/A
| Illuminated light switch mechanisms | N/A |  | Incomplete
A.9 Metering and Switchboard
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.12 14.4.13 | Customer metering requirements have been considered and appropriate provision made for their installation. Appropriate provisions made for the Customer Main Switchboard. | N/A
WASIR 14.3.4.1 | Customer Substations with more than 4MVA: The load is to be supplied from 2 evenly loaded fire rated switchboards with mechanical interlocking | N/A |  | Incomplete
A.10 Earthing
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.10 | The earthing system has been designed to ensure compliance with AS 2067, AS/NZS 3000 and the network operators requirements including the following: | N/A
| Earthing conductors are copper and sized in accordance with AS 2067 | N/A
| Earth connections are to be made in accordance with AS 2067 and AS/NZS 3000 | N/A
| Connections tagged and labelled | N/A
| Earth Bar location & adequate bonding | N/A
WASIR 14.4.10.3 | Dependent on location, EPR studies may be required for metallic structures/services around the substation site such as metallic pipelines, telecommunication services, metallic fences. | N/A
WASIR 14.6.3.1 | District or Sole Use Substation: Customer to arrange with the Network Operator to have the earth electrodes installed in the floor before pouring the concrete. | N/A
| Where remote earthing is designed: | N/A | N/A
| Earth pits | N/A
| Conduits | N/A
| Earth wire | N/A
WASIR 14.6.3.2 DSPM 3 | Customer Substation: Minimum of 2 earth electrodes is to be installed by the customer in the trench. For separate trenches, at least one electrode is required in each trench with a 75mm conduit to interconnect the electrodes | N/A |  | Incomplete
Distribution Conformance Assessment - Fire Rated Substation Installations
Part B - Construction
Purpose: To ensure the Design requirements in Part A have been Constructed and for any discrepancies to be addressed and rectified. Residual hazards to Western Power staff shall be adequately documented/managed for the life of the installation/asset.
PART B1 - PRE-INSTALLATION
I understand by signing below that the construction of the indoor substation meets the Western Power WASIR, WAER, AS/NZ standard requirements
Western Power (WP) Reference Number
Site Address
Name
Title
Company
Sign
Date
B.1.1 General Conditions
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
| Confirm that ALL requirements outlined in Part A have been met | N/A
WASIR 14.4.2 | Substation contains no building or other services apart from those shown on the drawings provided by the Network Operator. | N/A
WASIR 14.4.4 | Hazardous or flammable materials are not stored within the confines of a substation or its access and evacuation routes. | N/A
DPSM Section 3 | Minimum dimensions and arrangement as per the architect/site drawing. Identify the relevant DSPM drawing: | N/A
WASIR 14.6.11 | Fire rated certification provided | N/A
B.1.2 Access and Installation
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.7 | Confirm that 24/7 site access is suitable for heavy vehicles and plant, and that all access requirements have been considered, including: access route (slope/gradient), cable hauling/pulling eyes, gatic covers (if applicable) | N/A
AS2067 5.5.4 | Minimum access requirements maintained in service areas as per AS2067 5.5.4 where a non-standard design is proposed. | N/A
B.1.3 Emergency and Exit
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.4 | Requirements of fire alarm and fixed fire suppression systems are met. | N/A
WASIR 14.4.4.2 AS2419.1-2005 | Fire hydrants and brigade booster assemblies clearance from any HV distribution equipment (Provide clearance): | N/A
WASIR 14.4.4.3 | Petroleum and gas installations clearances from electrical equipment (Provide clearance): | N/A
WASIR 14.6.6 | Doors (2) are: | N/A | N/A
| Located on alternative walls (adequate separation) | N/A
| Self-closing/locking doors, fitted with panic release bars | N/A
| 2hr fire rated (including all associated hardware) | N/A
| Fitted with Network Operator labels as per AS/NZS 1905 | N/A
B.1.4 Civil and Structural
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.7 DSPM 3 | Minimum ceiling height: | N/A
| Roof to be dust tight | N/A
| All storm water guttering external to the room | N/A
AWASIR 14.3.4.1 DSPM 3 DSM 6 | HV/LV Switchgear and metering unit (if required) support structures have been supplied and installed. | N/A
B.1.5 Trenches, Ducts and Other Penetrations
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.2 | Trench surfaces and enclosure floors painted with an appropriate sealant | N/A
WASIR 6.10 DSPM 3 DSM 6 | Substation site has the correct cable duct arrangement, size and number: | N/A | N/A
| Power (including transformer tails) | N/A
| Earthing | N/A
| Communication (where required) | N/A
| Metering (where required) | N/A
B.1.6 Ventilation
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.7 AS2067 AS 1682 AS 3000 AS/NZS 1668 DSPM 3 DSM 6-02 | Ventilation installed as follows: | N/A | N/A
| Cooling | N/A | N/A
| Cross flow over transformers | N/A
| Fans located inside room. If forced, fan switch to be installed on the wall as per AS 3000 | N/A
| Dedicated inlet/outlet outside the building (basement OR non-boundary located) | N/A
| Individual (non-cumulative) ducting per transformer | N/A
| Vent/louvre number/size/type/positions | N/A
| Increased room height (3m) if ducting above transformer/RMU | N/A
| Thermostat to be installed directly above transformers and set to 50° | N/A
| Correct flow rate per transformer | N/A
| Fire/Smoke | N/A | N/A
| Self-closing pressure relief vents | N/A
| Ventilation system is 2hr fire rated | N/A
| Electrical | N/A | N/A
| Supplied from Substation Local DB | N/A
| Correct fan starter wiring | N/A
B.1.7 Light and Power
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.9 AS2067 Cl. 5.1.6 AS/NZS 1680 AS/NZS 3000 DSPM 3 | All general and emergency lighting fixtures, GPO’s (including additional automation GPO when required) including all associated wiring has been installed and tested. | N/A
| Substation Local DB (3ph) supplied from Customer SMSB (min. 6sq.mm) | N/A
| Illuminated light switch mechanisms | N/A
B.1.8 Earthing
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.3.1 | Identifiable location/labelling of (including remote): | N/A | N/A
| Earth pits | N/A
| Conduits | N/A
| Earth wire | N/A
WASIR 14.4.10 | Does the installation meet General Earthing Requirements, specifically Section 14.4.10.1? | N/A
DSPM 3 | Are all exposed metallic surfaces bonded to the substation earth bar as per DSPM Section 3, Sheet 5? | N/A
PART B2 - POST-INSTALLATION (to be completed by PNOs or SCS)
I understand by signing below that the construction of the indoor substation meets the Western Power WASIR, WAER, AS/NZ standard requirements
Western Power (WP) Reference Number
Site Address
Name
Title
Company
Sign
Date
B.2.1 Civil and Structural
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.5 DSPM 3 DSPM 5 | Substations housing a transformer have: | N/A | N/A
| Brick bund installed at least 75 mm high at every door location OR | N/A
| Alternative bunding | N/A
B.2.2 Trenches, Ducts and Other Penetrations
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.8 DSPM 3 | Appropriate trench covers: | N/A | N/A
| Installed correctly (mesh/slab) | N/A
| Supported correctly | N/A
| Fixed correctly | N/A
WASIR 14.6.8 | Ducts or other penetrations entering the trench or enclosure are: | N/A | N/A
| Fitted with removable watertight seals to both ends (earth rod penetrations single end only) | N/A
| 2hr fire rated sealed (including post-cable installation) | N/A
B.2.3 Earthing
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
AS 2067, AS/NZS 3000 | Earthing components: | N/A | N/A
| Earth bar correctly installed/located | N/A
| Connections tagged and labelled | N/A
| Bonding completed | N/A

## Sheet1 (hidden)
Conditional Formatting
N/A
Yes
No