## Outdoor Substation Checklist
Outdoor Substation Checklist v1.0
Distribution Conformance Assessment - Outdoor Substation Installations
Part A - Design
Purpose: To ensure the requirements for an outdoor substation installation have been met. The relevant sections of the WA Service & Installation Rules, Distribution Substation Plant Manual, Building Code of Australia and Australian Standards should be consulted for further information and clarity.
Instructions:
1. For each design requirement for PART A ONLY, select Yes, No, or N/A from the dropdown in column D
2. If you select No or N/A, provide a brief explanation in Column E
3. Complete all yellow sections until the status bar at the top indicates "Complete". Incomplete submissions may result in your application being rejected.
Last Updated | 11/07/2025 (Current)
Part A Status (Office use only) | Incomplete Sections Remaining
Site Address
Date
Name and Company
A.1 General Conditions
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 6.7.1 6.8 6.11 6.13 | Have the following matters been considered and addressed as part of the design preparation: | N/A | N/A
| Correct site identification (including final levels) | N/A
| Land allocation and easement/encumbrance requirements (eg. fire risk zone, cable route) | N/A
| Cable route | N/A
| Removal and reinstatement requirements for road reserves, public open space, etc. | N/A
| Environmental and heritage requirements | N/A
| Third Party approvals due to fire risk zone encroaching third party property. | N/A
WASIR 14.4.3 14.4.4 14.4.6 6.3.2 | A risk and hazard assessment has been undertaken including but not limited to the following: | N/A | N/A
| Location of other existing or proposed structures both on and adjacent to the site | N/A
| Identification of fire zones and fire escape routes | N/A
| Hazardous environments | N/A
| Climatic environmental conditions and flood levels | N/A
| Safety In Design | N/A
| Other matters (please state) | N/A
WASIR 14.4.2 | Substation contains no building (over) or other services (under) apart from those shown on the drawings provided by the Network Operator. | N/A
WASIR 14.4.2 | Does the enclosure comply with Government Agencies, Building Code of Australia and Local Government Authority requirements? | N/A |  | Incomplete
A.2 Site Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 12.5.3 14.4.6 14.2 14.3 | The selected site has been designed in accordance with the regulatory and network operators’ requirements including but not limited to acceptable: | N/A
| Substation type and substation arrangement | N/A
| Location above adjacent lots/roads, flood levels | N/A
| Location regarding water inundation and vegetation | N/A
| Site levels, compaction, stabilisation and soil erosion (where required engineering certified retaining walls, batters) | N/A
| Traffic movement and the need to provide infrastructure/equipment protection e.g. bollards | N/A
| Surface treatments (outdoor) | N/A |  | Incomplete
A.3 Access and Installation Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.7.1 14.4.7.2 14.4.7.3 | Confirm that site access is suitable for heavy vehicles and plant, and that all access requirements have been considered, including: access route (slope/gradient), cable hauling/pulling eyes, gatic covers (if applicable) | N/A
AS2067 5.5.4 | Minimum access requirements maintained in service areas as per AS2067 5.5.4 where a non-standard design is proposed | N/A
WASIR 14.2.1 | District Substations: Preferably situated on the front street boundary or by agreement with the Network Operator up to a maximum (LV Cable length) of 30m. | N/A |  | Incomplete
A.4 Emergency and Exit Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.4.2 AS2419.1-2005 | Fire hydrants and brigade booster assemblies are located in accordance with the standards (located 10m from any HV distribution equipment). | N/A
WASIR 14.4.4.3 | Petroleum and gas installations are located away from any Network Operator electrical equipment or as per WASIR distances. | N/A |  | Incomplete
A.5 Civil and Structural Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
DPSM Section 3 | Minimum dimensions and arrangement as per relevant DSPM Section 3 arrangement. | N/A
| Please detail relevant DSPM drawing | N/A
WASIR 14.4.10.3 14.4.11 14.5.4 DSPM 3 | Substation site screening requirements: | N/A | N/A
| Screening around the substation site (including fencing, walls, or vegetation) has been reviewed and approved by the network operator, and complies with safety, fire risk, and access requirements. | N/A |  | Incomplete
A.6 Trenches, Ducts and Other Penetrations
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 6.10 DSPM 3 DSM 6 | Substation site has the correct cable duct arrangement: | N/A | N/A
| Power cable | N/A
| Communication | N/A |  | Incomplete
A.7 Metering and Switchboard
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.12 14.4.13 | Customer metering requirements have been considered and appropriate provision made for their installation. Appropriate provisions made for the Customer Main Switchboard. | N/A |  | Incomplete
A.8 Earthing
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.10.3 | Dependent on location, EPR studies may be required for metallic structures/services around the substation site such as metallic pipelines, telecommunication services, metallic fences. | N/A |  | Incomplete
Distribution Conformance Assessment - Fire Rated Substation Installations
Part B - Construction
Purpose: To ensure the Design requirements in Part A have been Constructed and for any discrepancies to be addressed and rectified. Residual hazards to Western Power staff shall be adequately documented/managed for the life of the installation/asset.
PART B1 - PRE-INSTALLATION
I understand by signing below that the construction of the outdoor substation meets the Western Power WASIR, WAER, AS/NZ standard requirements
Western Power (WP) Reference Number
Site Address
Name
Title
Company
Sign
Date
B.1.1 General Conditions
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
| Confirm that ALL requirements outlined in Part A have been met | N/A
WASIR 14.4.2 | Substation contains no building or other services apart from those shown on the drawings provided by the Network Operator. | N/A
WASIR 14.4.4 | Hazardous or flammable materials are not stored within the confines of a substation or its access and evacuation routes. | N/A
DPSM Section 3 | Minimum dimensions and arrangement as per the architect/site drawing. Identify the relevant DSPM drawing: | N/A
WASIR 14.6.11 | Fire clearances/mitigation endorsed with Restrictive Covenant in place | N/A
B.1.2 Site Requirements
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.6.6 | The selected site has been prepared and constructed in accordance with the Network Operators requirements inclusive of: | N/A | N/A
| Soil compaction | N/A
| Erosion prevention measures | N/A
| Retaining walls/batters | N/A
| Fire clearances/mitigation | N/A
B.1.3 Access and Installation
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.7 | Confirm that 24/7 site access is suitable for heavy vehicles and plant, and that all access requirements have been considered, including: access route (slope/gradient), cable hauling/pulling eyes, gatic covers (if applicable) | N/A
AS2067 5.5.4 | Minimum access requirements maintained in service areas as per AS2067 5.5.4 where a non-standard design is proposed. | N/A
B.1.3 Emergency and Exit
Reference | Substation Design Requirements | Yes/No | Explanation Please provide for No or N/A responses
WASIR 14.4.10.2 | For outdoor HV connections, the earthing installation is tested and commissioned in accordance with the requirements of AS 2067, AS/NZS 3000 and as specified by the Network Operator. Test results have been provided to Construction Project Manager. | N/A

## Sheet1 (hidden)
Conditional Formatting
N/A
Yes
No